AST/RO OBSERVATORY DESCRIPTION AND REQUIREMENTS

- THIS BUILDING IS A ROLL RETRACTABLE OBSERVATORY TO HOUSE THE AST/RO SUB MILLIMETER RADIO TELESCOPE AS WELL AS THE NECESSARY SUPPORT EQUIPMENT.  IT WILL ULTIMATELY BE INSTALL ON THE ATACAM A PLATEAU IN CHILE.  IT WILL BE TEMPORARY INSTALLED ON THE OBERLIN COLLEGE CAMPUS FOR COMMISSIONING.

- SINCE THIS FACILITY WILL BE REMOTELY OPERATED ALL DESIGNS MUST MAXIMIZE RELIABILITY.

- THE ARRANGEMENT SHOWN IS CONCEPT ONLY.

- THE BUILDING TO BE DESIGNED WITH BOLT TOGETHER SECTIONS TO FIT INTO A SHIPPING CONTAINER.

- LIGHTING WILL BE PROVIDED IN EACH OF THE THREE AREAS.  WIRING TO BE VIA PLUG-IN CABLES

- WALL RECEPTACLES TWO IN THE TELESCOPE ROOM, FOUR IN THE UTILITY ROOM, AND TWO IN THE CRYOGENIC ROOM

- THE TELESCOPE FOUNDATION WILL LIMIT THE DEFLECTION TO 3 ARC SECONDS WHEN A 100 POUND HORIZONTAL LOAD IS APPLIED

- CONTROL PANEL BY OTHERS

- POWER PANEL WILL RECEIVE 220 V 3Y AND CONTAIN THE FOLLOWING CIRCUITS:

  - 100 AMP 220 3 Y FOR CONTROL PANEL POWER

  - THREE 15 AMP  120 V LIGHTING CIRCUITS

  - THREE 20 AMP 120 V WALL PLUG CIRCUITS

  - 50 AMP 120 V CONTROL PANEL POWER

  - 20 KVA 220V-120V TRANSFORMER

- RETRACTABLE ROOF TO BE ELECTRICALLY OPERATED WITH REDUNDANT IN-POSITION LIMIT SWITCHES.  ROLL OFF TIME TO BE LESS THAN ONE MINUTE. (STARTER BY OTHERS)

- THE ACCESS DOOR TO THE TELESCOPE ROOM WILL BE INTERLOCKED WITH A KIRK-KEY SYSTEM OR EQUIVALENT (WIRING BY OTHERS)